## Metric-GlobalTrac-China
更改表格中标黄的数值，以针对不同缆线半径或填充率估算缆线填充值。
CPI 缆线管理和路径产品的估算缆线填充容量
产品型号 | 描述 | 理线器规格 |  |  |  | 建议缆线填充 |  |  | 最大缆线填充 |  |  | Recommended Cable Fill | [5 empty] | Maximum Cable Fill
|  | 内宽 （毫米） | 内深 （毫米） | 可用面积 （平方毫米) | 缆线 | Cat 5e | Cat 6 | Cat 6a | Cat 5e | Cat 6 | Cat 6a
[5 empty] | 外径（毫米） | 5.08 | 6.35 | 7.62 | 5.08 | 6.35 | 7.62 | 5.08 |  | 6.35 |  | 7.62 |  | 5.08 |  | 6.35 |  | 7.62
[5 empty] | 填充率 | 50% | 50% | 50% | 100% | 100% | 100% | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
适用于机架和机柜机箱的垂直理线器
84897-703 | Momentum 带环垂直理线器，黑色 | 107 | 89 | 9480 |  | 116 | 74 | 51 | 233 | 149 | 103
84898-001 | Momentum 垂直理线器 D 型环组件，黑色 | 107 | 218 | 23290 |  | 287 | 183 | 127 | 574 | 367 | 255
GT 系列 GlobalFrame® 机柜系统
25088-7XX | GT-系列 GlobalFrame, 顶板，圆形缆线孔，一个. | 69 mm Ø | N/A | 3806 |  | 46 | 30 | 20 | 93 | 60 | 41 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25088-7XX | GT-系列 GlobalFrame, 顶板，大型缆线孔，一个 | 99 | 223 | 22141 |  | 273 | 174 | 121 | 546 | 349 | 242 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25104-001 | GT-系列 GlobalFrame, 理线环组件，针对 600 mm 宽机柜 | 25 | 112 | 2800 |  | 34 | 22 | 15 | 69 | 44 | 30 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25106-001 | GT-系列 GlobalFrame, 理线环组件，含大型理线环， 针对 600 mm 宽机柜 | 107 | 218 | 23290 |  | 287 | 183 | 127 | 574 | 367 | 255 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25106-002 | GT-系列 理线环组件, 理线环组件，含中型理线环， 针对 800 mm 宽机柜 | 107 | 89 | 9523 |  | 117 | 75 | 52 | 234 | 150 | 104 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25107-001 | GT-系列 GlobalFrame, 嵌入式垫环组件，1 个垫环 | 81 | 139 | 11354 |  | 140 | 89 | 62 | 280 | 179 | 124 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25108-001 | GT-系列 GlobalFrame, 嵌入式垫环和栓塞组件，1 个垫环 | 81 | 139 | 11354 |  | 140 | 89 | 62 | 280 | 179 | 124 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25110-700 | GT-系列 GlobalFrame, 垂直理线器，含标准销，针对 42U x 600 mm 宽机柜 | 25 | 155 | 3875 |  | 47 | 30 | 21 | 95 | 61 | 42 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25120-706 | GT-系列 GlobalFrame, 垂直理线器，含扩展销，针对 42U x 800 mm 宽机柜 | 123 | 215 | 26445 |  | 326 | 208 | 144 | 652 | 417 | 289 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25130-7XX | GT-系列 GlobalFrame, ，底板，缆线孔，一个 | 223 | 99 | 22141 |  | 273 | 174 | 121 | 546 | 349 | 242 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25380-XXX | GT-系列 GlobalFrame, 大型缆线孔，一个 | 99 | 226 | 22393 |  | 276 | 176 | 122 | 552 | 353 | 245 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25402-700 | GT-系列 GlobalFrame, 理线环的理线器，含大型理线环， 针对 42U x 800 mm 宽机柜 | 107 | 218 | 23290 |  | 287 | 183 | 127 | 574 | 367 | 255 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25402-701 | GT-系列 GlobalFrame, 理线环的理线器，含中型理线环， 针对 42U x 800 mm 宽机柜 | 107 | 89 | 9523 |  | 117 | 75 | 52 | 234 | 150 | 104 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25403-701 | GT-系列 GlobalFrame, 缆线捆扎托架，42U x 125 mm | 125 | 50 | 6250 |  | 77 | 49 | 34 | 154 | 98 | 68 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25404-706 | GT-系列 GlobalFrame, 垂直理线器，含标准销， 针对 42U x 800 mm 宽机柜 | 123 | 155 | 19065 |  | 235 | 150 | 104 | 470 | 301 | 209 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25873-701 | GT-系列 GlobalFrame, FTR 理线器，800mm 机柜 | 99 | 124 | 12276 |  | 151 | 96 | 67 | 302 | 193 | 134 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
DistributionFrame 机柜系统
14068-701 | DistributionFrame, 理线环配件组件，1 个环 | 57 | 139 | 7923 |  | 97 | 62 | 43 | 195 | 125 | 86 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25844-70X | DistributionFrame，缆线捆扎托架，针对 42U | 125 | 25 | 3125 |  | 38 | 24 | 17 | 77 | 49 | 34 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25857-001 | DistributionFrame, 设备导轨垫环套件，1 个垫环 | 43 | 127 | 5461 |  | 67 | 43 | 29 | 134 | 86 | 59 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
25875-70X | DistributionFrame, FTR 理线器，800mm 机柜 | 46 | 61 | 2806 |  | 34 | 22 | 15 | 69 | 44 | 30 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
GlobalTrac 金属网格式缆线桥架产品
GlobalTrac 缆线桥架侧墙有 50 mm、100 mm 或 150 mm 高三种规格。缆线不应超过桥架高度。
84811-X02 | GlobalTrac 缆线桥架, 50 mm 高 x 50 mm 宽 x 3 m 长 | 50 | 50 | 2500 |  | 30 | 19 | 13 | 61 | 39 | 27 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84811-X04 | GlobalTrac 缆线桥架, 50 mm 高 x 100 mm 宽 x 3 m 长 | 100 | 50 | 5000 |  | 61 | 39 | 27 | 123 | 78 | 54 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84811-X06 | GlobalTrac 缆线桥架, 50 mm 高 x 150 mm 宽 x 3 m 长 | 150 | 50 | 7500 |  | 92 | 59 | 41 | 185 | 118 | 82 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84811-X08 | GlobalTrac 缆线桥架, 50 mm高 x 200 mm 宽 x 3 m 长 | 200 | 50 | 10000 |  | 123 | 78 | 54 | 246 | 157 | 109 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84811-X12 | GlobalTrac 缆线桥架, 50 mm高 x 300 mm 宽 x 3 m 长 | 300 | 50 | 15000 |  | 185 | 118 | 82 | 370 | 236 | 164 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84811-X16 | GlobalTrac 缆线桥架, 50 mm 高 x 400 mm 宽 x 3 m 长 | 400 | 50 | 20000 |  | 246 | 157 | 109 | 493 | 315 | 219 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84811-X18 | GlobalTrac 缆线桥架, 50 mm 高 x 450 mm 宽 x 3 m 长 | 450 | 50 | 22500 |  | 277 | 177 | 123 | 555 | 355 | 246 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84811-X20 | GlobalTrac 缆线桥架, 50 mm高 x 500 mm 宽 x 3 m 长 | 500 | 50 | 25000 |  | 308 | 197 | 137 | 616 | 394 | 274 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84811-X24 | GlobalTrac 缆线桥架, 50 mm 高 x 600 mm 宽 x 3 m长 | 600 | 50 | 30000 |  | 370 | 236 | 164 | 740 | 473 | 328 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84821-X04 | GlobalTrac 缆线桥架, 100 mm高 x 100 mm宽 x 3 m 长 | 100 | 100 | 10000 |  | 123 | 78 | 54 | 246 | 157 | 109 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84821-X06 | GlobalTrac 缆线桥架, 100 mm 高 x 150 mm宽 x 3 m长 | 150 | 100 | 15000 |  | 185 | 118 | 82 | 370 | 236 | 164 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84821-X08 | GlobalTrac 缆线桥架, 100 mm 高 x 200 mm宽 x 3 m 长 | 200 | 100 | 20000 |  | 246 | 157 | 109 | 493 | 315 | 219 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84821-X12 | GlobalTrac 缆线桥架, 100 mm 高 x 300 mm W x 3 m 长 | 300 | 100 | 30000 |  | 370 | 236 | 164 | 740 | 473 | 328 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84821-X16 | GlobalTrac 缆线桥架, 100 mm高 x 400 mm W x 3 m 长 | 400 | 100 | 40000 |  | 493 | 315 | 219 | 986 | 631 | 438 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84821-X18 | GlobalTrac 缆线桥架, 100 mm 高 x 450 mm W x 3 m长 | 450 | 100 | 45000 |  | 555 | 355 | 246 | 1110 | 710 | 493 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84821-X20 | GlobalTrac 缆线桥架, 100 mm 高 x 500 mm W x 3 m长 | 500 | 100 | 50000 |  | 616 | 394 | 274 | 1233 | 789 | 548 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84821-X24 | GlobalTrac 缆线桥架, 100 mm 高 x 600 mm W x 3 m长 | 600 | 100 | 60000 |  | 740 | 473 | 328 | 1480 | 947 | 657 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84821-X28 | GlobalTrac 缆线桥架, 100 mm 高 x 700 mm W x 3 m长 | 700 | 100 | 70000 |  | 863 | 552 | 383 | 1726 | 1105 | 767 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84821-X32 | GlobalTrac 缆线桥架, 100 mm 高 x 800 mm W x 3 m长 | 800 | 100 | 80000 |  | 986 | 631 | 438 | 1973 | 1263 | 877 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84821-X36 | GlobalTrac 缆线桥架, 100 mm 高 x 900 mm W x 3 m长 | 900 | 100 | 90000 |  | 1110 | 710 | 493 | 2220 | 1420 | 986 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84831-X06 | GlobalTrac 缆线桥架, 150 mm 高 x 150 mm W x 3 m 长 | 150 | 150 | 22500 |  | 277 | 177 | 123 | 555 | 355 | 246 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84831-X08 | GlobalTrac 缆线桥架, 150 mm 高 x 200 mm W x 3 m 长 | 200 | 150 | 30000 |  | 370 | 236 | 164 | 740 | 473 | 328 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84831-X12 | GlobalTrac 缆线桥架, 150 mm 高 x 300 mm W x 3 m 长 | 300 | 150 | 45000 |  | 555 | 355 | 246 | 1110 | 710 | 493 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84831-X16 | GlobalTrac 缆线桥架, 150 mm 高 x 400 mm W x 3 m 长 | 400 | 150 | 60000 |  | 740 | 473 | 328 | 1480 | 947 | 657 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84831-X18 | GlobalTrac 缆线桥架, 150 mm 高 x 450 mm W x 3 m 长 | 450 | 150 | 67500 |  | 832 | 532 | 370 | 1665 | 1065 | 740 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84831-X20 | GlobalTrac 缆线桥架, 150 mm高 x 500 mm W x 3 m长 | 500 | 150 | 75000 |  | 925 | 592 | 411 | 1850 | 1184 | 822 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84831-X24 | GlobalTrac 缆线桥架, 150 mm 高 x 600 mm W x 3 m 长 | 600 | 150 | 90000 |  | 1110 | 710 | 493 | 2220 | 1420 | 986 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84831-X28 | GlobalTrac 缆线桥架, 150 mm 高 x 700 mm W x 3 m 长 | 700 | 150 | 105000 |  | 1295 | 828 | 575 | 2590 | 1657 | 1151 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84831-X32 | GlobalTrac 缆线桥架, 150 mm 高 x 800 mm W x 3 m 长 | 800 | 150 | 120000 |  | 1480 | 947 | 657 | 2960 | 1894 | 1315 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
84831-X36 | GlobalTrac 缆线桥架, 150 mm 高 x 900 mm W x 3 m 长 | 900 | 150 | 135000 |  | 1665 | 1065 | 740 | 3330 | 2131 | 1480 | 20.268 | 50% | 31.669 | 50% | 45.603 | 50% | 20.268 | 100% | 31.669 | 100% | 45.603 | 100%
注意： | 本表列示的估算缆线填充值针对 CPI GlobalTrac 金属网格式缆线桥架产品。缆线填充值根据缆线尺寸而变化。
缆线填充值按外径 5.08 mm Cat 5e、外径 6.35 mm Cat 6 和 外径 7.62 mm Cat 6a、4 对 UTP 缆线进行估算。
使用 Cat 5e 的数值估算 6 股光纤的填充值。使用 Cat 6e 的数值估算 12 股光纤的填充值。
建议缆线桥架/最大缆线填充按 TIA-569 建议值和 1.5 m 支架间距计算。
部件号一栏中的 X 代表颜色或不影响缆线填充能力的另一型号。请参阅 CPI 迷你目录以了解可用选项。
计算其他尺寸缆线的建议缆线填充值时，用产品可用面积除以缆线面积再乘以 25% （最大填充乘以 50%）。
尽管已采取一切措施确保所有信息的准确性，但 CPI 对任何错误或疏漏不承担责任，并且保留修改所列服务及产品的信息和描述的权利。
美国及加拿大地区以外有售.
©2013 Chatsworth Products, Inc. 保留所有权利。CPI、CPI Passive Cooling、GlobalFrame、MegaFrame、Saf-T-Grip、Seismic Frame、SlimFrame、TeraFrame、Cube-iT Plus、 Evolution、OnTrac、Velocity 和 QuadraRack 是 Chatsworth Products, Inc. 的联邦注册商标。eConnect 和 Simply Efficient 是 Chatsworth Products 的商标。 所有其他商标归其各自公司所有。 10/13
Note on H6: CPI estimates cable fills with the following values: 5.080 mm (.20") OD for Cat 5e 4-pair UTP 6.35 mm (.25") OD for Cat 6 4-pair UTP 7.62 mm (.30") OD for Cat 6a 4-pair UTP Calculations assume round cables. Change the values to match your cable to estimate more accurate cable fills. Enter the outside diameter of the cable in millimeters.
Note on H7: Enter fill ratio as a percentage. 50% fill is recommended for planning. 100% is the maximum fill. If you enter a fill ratio that exceeds the maximum fill, the value for the maximum fill will be returned.

## MethodOfCalculation-GlobalTrac
Using the CPI CABLE FILL TABLE:
Change the OD (outside diameter) of the cable or the fill ratio on the table to estimate fills
for your application. Fill ratio is the percentage of Usable Area within the manager filled
with cable including gaps between cables.
Method of Calculation
Cable Fill is calculated by dividing the usable area of the cable tray by the area of the cable
and reducing by a 50% fill factor to allow for gaps between the cables.
The basic calculation for estimating recommended cable fill for cable managers and cable pathway is:
RECOMMENDED CABLE FILL = ((USABLE AREA/AREA OF CABLE) X 50%) X 50%
50% is the fill ratio (25% of the manager is filled with cable. 25% is required space between cables.)
The basic calculation for estimating maximum cable fill for cable managers and cable pathway is:
MAXIMUM CABLE FILL = (USABLE AREA/AREA OF CABLE) X 50%) X 100%
100% is the fill ratio. (50% of the manager is filled with cable. 50% is required air space between cables.)
USABLE AREA is the Usable Area of the cable manager or pathway product.
Usable Area is determined by measuring the internal width and
depth of the tray or manager.
The CPI Cable Fill table lists usable areas for CPI GlobalTrac Wire Mesh Cable Tray products.
The area of a rectangular space is calculated by multiplying
the width by the depth. In some cases the width of the manager varries:
USABLE AREA = INTERIOR WIDTH X INTERIOR DEPTH
AREA OF CABLE is the area of the cable. The table assumes round cables.
The area of the cable is calculated using the dimensions of the cable.
To determine the values in the CPI Cable Fill table, average
cable sizes are used to represent each type of cable:
Cat 5e is 5.08 mm diameter cable, which has a 20.268 mm² area
Cat 6 is 6.35 mm diameter cable, which has a 31.669 mm² area
Cat 6a is 7.62 mm diameter cable, which has a 45.603 mm² area
The area of a round cable is calculated by multiplying PI and
the radius of the cable squared:
(ROUND) CABLE AREA = PI X RADIUS2
FILL RATIO is the percentage of Usable Area within the manager that is filled with cable including
required gaps between cables.
CABLE FILL is the calculated cable fill value. This value is an estimate and includes gaps between
cables. Use 100% fill ratio to estimate maximum fill. Use 50% fill ratio to extimate initial fill.
This estimate represents loose cables, not bundled cables. The value will be less for bundled cables.
Sample Cable Fill Calculation:
Calculate cable fill of 7.62 mm OD Cat 6a UTP in CPI GlobalTrac Wire Mesh Cable Tray (P/N 84811-X02).
CPI P/N 84811-X02 has a usable area of 2500 mm²
7.62 mm OD Cable has an area of 45.603 mm²; Area = Pi x [3.81]²
RECOMMENDED CABLE FILL = ((USABLE AREA/AREA OF CABLE) X 50%) X 50%
RECOMMENDED CABLE FILL = ((2500 mm²/45.603 mm²) x 50%) x 50%
RECOMMENDED CABLE FILL = 13 cables
MAXIMUM CABLE FILL = ((USABLE AREA/AREA OF CABLE) X 50%) X 100%
MAXIMUM CABLE FILL = ((2500 mm²/45.603 mm²) x 50%) x 100%
MAXIMUM CABLE FILL = 27 cables